## Builders Work
Council of the Isles of Scilly
Off Island Toilets and Fire Station
Schedule of Works
Bryher Fire Station - Builders Work
Duplicated work item
Ref | Description | Quantity | Unit | Rate | £
External
3.2.1 | Slate roof covering repairs Allow to supply and install replacement slates to match existing where slipped, cracked or damaged. Provisionally allow to replace: 30nr slates |  | Item
3.2.2 | Flashing missing and defective section to vehicle shed. Allow to strip back and re-dress with new lead and lap with tiles to provide appropriate weather seal. Lead to meet BS EN 12588. Supply and install new code 4 lead step and cover flashing. Minimum 100mm laps. New lead to be chased into masonry brick joint by 25mm minimum. Point in flashing using pointing sealant/mortar approved by manufacturer. Cover flashing to be installed minimum 75mm above intersection with abutment and provide minimum of 150mm cover to roof. Provisionally allow for: 5l/m |  | Item
3.2.3 | Verge/abutment detailing above crew room poor and allows route for water ingress Allow to strip back and re-dress with new lead and lap with tiles to provide appropriate weather seal. Lead to meet BS EN 12588. Supply and install new code 4 lead step flashing. Minimum 100mm laps. New lead to be chased into masonry brick joint by 25mm minimum. Point in flashing using pointing sealant/mortar approved by manufacturer. Provisionally allow for: 5l/m |  | Item
3.2.4 | Damp timbers to main roof structure Provisionally allow for localised structural timber repairs and treatment to main roof structure. |  | Provisional Sum |  | 2500
3.2.5 | Corrugated roof covering removal (possibly asbestos) Subject to confirmation of asbestos, carefully remove and dispose of using licenced removal contractor. Provisionally allow for an area of: 10m² Upon removal of the roof covering, the contractor is to inform the CA of the build-up and condition of the existing roof structure. Existing structure to be assessed for strength and condition to ensure appropriate strengthening / repair / treatment as required. Contractor to ensure adequate weather protections is provided for the duration of exposed works to prevent water ingress. |  | Item
3.2.6 | Corrugated roof covering replacement – potential structural works Provisionally allow to renew roof structure. Truss Spans assumed as, 1.5 and 3m lengths. Allow to supply and install: - 6no. C16: 44 x 150mm rafters - Rafters installed at 400mm centres - 2no. 50 x 75mm wall plates bed into mortar - Galvanised steel wall plate straps - 1no. 150 x 25mm ridge board |  | Item
3.2.7 | Corrugated roof covering replacement Allow to supply and install Kingspan “KS1000SRW” or similar approved insulated, profiled roof panels to include ridge, verge and abutment detailing in accordance with manufacturers recommendations. - Material: Metallic protected steel to BS EN 10346: 2015 - Insulation thickness: 60mm to achieve u-value of 0.32W/m²K - Finish: TBC Provisionally allow for: 10m² |  | Item
3.2.8 | External wall render repairs and redecorations Allow to make localised repairs, rake out and fill isolated hairline cracking and redecorate to match existing. Refer to ‘External Redecorations – Masonry Surfaces’ specification item 4.0. |  | Item
3.2.9 | Vehicle shed doors heavily weathered Contractor to redecorate previously painted timber elements to vehicle shed doors. Refer to ‘External Redecorations – Timber Surfaces’ specification item 5.0. Allow for internal redecoration to the inner face of the windows and doors using a Dulux trade paint to match the existing finishes. Allow for localised repairs to timbers and easing and adjusting to ensure smooth operation of opening parts upon completion. |  | Item |  |  | 0
3.2.10 | Pedestrian doors heavily weathered Contractor to redecorate previously painted timber elements to pedestrian external doors. Refer to ‘External Redecorations – Timber Surfaces’ specification item 5.0. Allow for internal redecoration to the inner face of the windows and doors using a Dulux trade paint to match the existing finishes. Allow for localised repairs to timbers and easing and adjusting to ensure smooth operation of opening parts upon completion. |  | Item
3.2.11A | Windows heavily weathered – Cost Option A Allow to overhaul windows with localised timber repairs, replace blown glazing units. Service openings and replace ironmongery where necessary to ensure smooth operation. Redecorate previously painted external timber surfaces. Refer to ‘External Redecorations – Timber Surfaces’ specification item 5.0. Colours to match existing. Allow for internal redecoration to the inner face of the windows and doors using a Dulux trade paint to match the existing finishes. |  | Cost Option
3.2.11B | Windows heavily weathered – Cost Option B Replacement of existing windows with new PVCu windows. Contractor is to conduct survey and measure openings prior to order in accordance with BS 8213-4:2016 and provide costed breakdown summary. Carefully remove and dispose of all windows and make good areas. Supply and install Veka M70 PVCu windows or similar approved. Following hinges and locking mechanisms to be supplied with the windows or similar approved must be minimum Austenitic Stainless - Hinges: Securistyle Defender Hinge (Austenitic Stainless) - Locking mechanism: Securistyle Defender Locking Mechanism (Austenitic Stainless) Existing opening configurations to match existing. Installation to be in accordance with manufactures instructions. Upon completion allow for final check / adjusting / lubricating on all components to ensure correct operation and make good to surrounding surfaces. |  | Cost Option
3.2.12 | Timber fascia/soffit boards weathered exhibiting decay Allow to carefully remove uPVC guttering and fixtures and set aside for later re-use. Remove rotten sections of timber fascia/soffit boards and replace with new timber to match existing. Allow for localised timber repair and treatment. Provisional allow for: 10 l/m Allow to redecorate all timber fascia’s and soffits to achieve uniform appearance, colour: white. Refer to ‘External Redecorations – Timber Surfaces’ specification item 5.0. Contractor to provide cost per l/m for over capping with white uPVC fascia and soffits: ________ l/m |  | Item
3.2.13 | Rainwater goods localised defects, misalignment Allow to re-instate uPVC guttering and fixtures, ensuring downpipes are aligned correctly to existing underground drainage and guttering laid to appropriate falls. Allow for 25% guttering replacement to match existing surrounding. |  | Item
0
3.2.14 | External ventilation bricks blocked by grassed area vegetation and debris Allow to reduce level of grassed area to perimeter of the building to ensure sub-void is ventilated at all times. Clear vegetation and debris from ventilation bricks. |  | Item
Internal
3.2.15 | Sanitaryware soiled and worn - Strip-out Allow to decommission existing sanitary installations and strip out all WC’s, urinals, sinks, associated pipework, cubicles, soap dispensers and hand dryers and dispose from site. Contractor to notify CA of any additional fixtures and fittings within WC’s for removal instructions. |  | Item
3.2.16 | No insulation above main hall space Allow to supply and install 270mm of mineral wall insulation to roof void above hall space. Ensure insulation is installed to an even coverage. |  | Item
0
3.2.17 | Concrete flooring to entrance area and rear exit worn Allow to reseal concrete floors with ‘Smart Seal Concrete Floor Sealer’ for internal domestic & commercial use in strict accordance with manufacturers instructions or similar approved. Ensure application areas are sufficiently prepared prior to application. Give concrete floor thorough clean, brush down and wash with detergent. Ensure the floor is clean, free from anything that may interfere with adhesion of applied coating and sufficiently dry. Contractor to liaise with building occupier for removal of equipment and furniture in advanced of works programme. |  | Item
3.2.18 | Steps do not have contrasting colour to floors Allow to supply and install adhesive hi-visibility stair nosings to steps. |  | Item
3.2.19 | Vinyl flooring to WC’s and Office heavily stained and rucking Allow to strip and dispose of existing vinyl floor coverings. Supply and install new ‘Altro Aquaris Safety Flooring’ or similar approved in strict accordance with manufacturer’s instructions. Allow for the preparation of sub-base in accordance with manufactures recommendations. |  | Item
3.2.20 | Timber flooring to crew room staining and worn Allow to replace rotten timber floorboards. Provisionally allow for: 5l/m Upon removal, inspect existing sub-floor ventilation and report findings back to CA. Allow to stain timber floors to achieve uniform finish. Product: Contractors choice, submit proposal for approval. |  | Item
3.2.21 | Ceilings (timber panelled) - Approximately 10% of timber panels to ceilings rotten requiring replacement. Allow to replace rotten timbers with new to match existing. To new and existing panelling. Allow to redecorate to achieve uniform appearance. Colour: white, to match existing. Product: Contractors choice, submit proposal for approval. |  | Item
3.2.22 | Ceilings (plastered and painted surfaces) – Damp staining and mould build-up Upon resolution of sources of water ingress, promote rapid drying to rooms subject to dampness and mould. To areas subject to mould growth apply ‘Granocryl Fungicidal Wash’ or similar approved (suitable for internal use) in strict accordance with manufactures instructions. Allow for the stated drying out time. Prepare surfaces and redecorate ceilings with ‘Dulux Matt’ finish colour: White, to match existing. |  | Item
3.2.23 | Minor cracking, damp staining and peeling to internal walls To areas exhibiting hairline cracking, rake out cracks, and repair using ‘Gyproc EasiFill 60’ filler in accordance with manufacturers recommendations. Prepare surface by removing loose and friable material. Fill cracks and bring flush to surrounding surfaces and allow to cure. Sand down to smooth finish to receive decoration. To areas subject to mould growth apply ‘Granocryl Fungicidal Wash’ or similar approved (suitable for internal use) in strict accordance with manufactures instructions. Allow for the stated drying out time. Prepare surfaces and redecorate internal walls with ‘Dulux Trade Matt’ finish colour: White, to match existing and achieve uniform finish. |  | Item

## Plumbing & Mechanical
Council of the Isles of Scilly
Off Island Toilets and Fire Station
Schedule of Works
Bryher Fire Station - Plumbing
Duplicated work item
Ref | Description | Quantity | Unit | Rate | £
3.2.15 | Sanitaryware soiled and worn - Strip-out Allow to decommission existing sanitary installations and strip out all WC’s, urinals, sinks, associated pipework, cubicles, soap dispensers and hand dryers and dispose from site. Contractor to notify CA of any additional fixtures and fittings within WC’s for removal instructions. |  | Item
3.2.24 | Sanitaryware installations - Replacement Contractor to submit proposal for approval to include full sanitaryware replacement including toilets, sinks and urinals with all associated pipework and fixtures to match existing arrangements and capacity. Design must incorporate water saving measures such as low flushing services, tap aerators and waterless urinals. Ideal Standard Ltd (Armitage Shanks) suite of products or similar approved. Web: https://www.armitageshanks-mena.com/homepage.html Toilets - Type: Close-coupled, Floor mounted - Material: Vitreous China, white BS 3402 - Flush: Push-button Sinks - Type: Wall mounted - Taps: Self-closing pillar taps - Material: Vitreous China, white BS 3402 Urinals - Type: Wall mounted - Waste: Waterless urinal, concealed waste - Material: Vitreous China, white BS 3402 |  | Contractors Design
3.2.29 | Sink - Point of use hot water heater not working Supply and install new point of use hot water heater to sink. |  | Contractors Design
3.2.30 | Blue MDPE pipe not suitable for above ground distribution. Allow to replace with insulated copper pipework including fixtures/fittings. |  | Contractors Design
3.2.31 | Bathroom mechanical extract not working Allow to supply and install new mechanical extract fan on the external facing wall to achieve a minimum extract rate of 15L/s to meet the guidance in Approved Document F. Make good the area around any penetrations internally and externally. |  | Contractors Design
3.2.32 | No mechanical ventilation installed to the galley kitchen Allow to supply and install new mechanical extract fan including penetration through wall fabric to achieve a minimum extract rate of 30L/s to meet the guidance in Approved Document F. Make good the area around any penetrations internally and externally. |  | Contractors Design
3.2.34 | Taps to galley sink corroded. Allow to replace galley sink taps with new, stainless-steel taps. |  | Contractors Design
3.2.37 | No backflow protection to hose Provide backflow protection to hose connection. |  | Contractors Design
0
0
0

## Electrical
Council of the Isles of Scilly
Off Island Toilets and Fire Station
Schedule of Works
Bryher Fire Station - Electrical
Duplicated work item
Ref | Description | Quantity | Unit | Rate | £
3.2.25 | Incoming LV ducts require sealing to prevent vermin access Seal LV ducts. Contractor to submit proposal for approval. |  | Contractors Design
3.2.26 | PVC Distribution Board Allow to replace PVC distribution board with metal fireproof board in accordance with BS 7671. |  | Contractors Design
3.2.27 | Internal light fittings missing diffusers and no emergency lighting. Allow to supply and install diffusers to light fittings. Contractors design, supply and install new emergency lighting layout. |  | Contractors Design
3.2.28 | Socket outlets in poor condition Allow to replace socket outlets. |  | Contractors Design
3.2.29 | Sink - Point of use hot water heater not working Supply and install new point of use hot water heater to sink. |  | Contractors Design
3.2.33 | Electric heaters past economic life and poor condition Allow to strip and dispose of existing heat emitters. Supply and install new electric heat emitters to match existing configuration. Heater to be: Messrs, Dimplex, Millbrook House, Grange Drive, Hedge End, Southampton, Hampshire, S030 2DF, telephone, 0844 879 3589, being the Quantum Range. |  | Contractors Design
3.2.35 | LV cable supplying ambulance station is not fit for purpose Allow to replace cable and install appropriate containment. |  | Contractors Design
3.2.36 | External lighting degraded Allow to replace external lighting to match existing output and configuration. |  | Contractors Design
3.2.38 | Lightning protection Provisionally allow to install lightening and surge protection in accordance with BS EN 52306 and BS 7671. |  | Contractors Design |  |  | 0
0
0