## Builders Work
Council of the Isles of Scilly
Off Island Toilets and Fire Station
Schedule of Works
St Agnes Fire Station - Builders Work
Duplicate item of work
Ref | Description | Quantity | Unit | Rate | £
External
3.7.1 | Corrosion to roller shutter laths Provisionally allow to replace laths and overhaul shutter door. Works subject to instruction by CA following recommendations by Dorma (scheduled w/c 1st August). |  | Provisional Sum |  | 2000
3.7.2 | Timber skirt around perimeter of building heavily weathered Allow to strip and dispose of existing timber skirting. Supply and install new 18mm WPB Hardwood Plywood Sheet to external skirt perimeter. Upon installation, treat plywood with Safeguard “Roxil Wood Preserver” in accordance with manufacturers recommendation www.safegaurdeurope.com or similar approved. |  | Item
3.7.3 | Timber framed windows, windowsills and entrance door minor weathering Allow to redecorate previously painted timber surfaces to windows and doors. Refer to ‘External Redecorations – Timber Surfaces’ specification item 4.0. Contractor to make allowance for easing and adjusting to ensure smooth operation of moving parts. |  | Item
Internal
3.7.4 | Concrete flooring minor surface damage and wear Allow to reseal concrete floors with ‘Smart Seal Concrete Floor Sealer’ for internal domestic & commercial use in strict accordance with manufacturer’s instructions or similar approved. Ensure application areas are sufficiently prepared prior to application. Give concrete floor thorough clean, brush down and wash with detergent. Ensure the floor is clean, free from anything that may interfere with adhesion of applied coating and sufficiently dry. Contractor to liaise with building occupier for removal of equipment and furniture in advanced of works programme. |  | Item
3.7.19 | Bathroom mechanical extract not working Allow to supply and install new mechanical extract fan on the external facing wall to achieve a minimum extract rate of 15L/s to meet the guidance in Approved Document F. Make good the area around any penetrations internally and externally. |  | Item
3.7.20 | No mechanical ventilation installed to the galley kitchen Allow to supply and install new mechanical extract fan including penetration through wall fabric to achieve a minimum extract rate of 30L/s to meet the guidance in Approved Document F. Make good the area around any penetrations internally and externally. |  | Item

## Plumbing & Mechanical
Council of the Isles of Scilly
Off Island Toilets and Fire Station
Schedule of Works
St Agnes Fire Station - Plumbing
Duplicate item of work
Ref | Description | Quantity | Unit | Rate | £
3.7.14 | Blue MDPE pipe not suitable for above ground distribution. Allow to replace with insulated copper pipework including fixtures/fittings. |  | Item
3.7.15 | No backflow protection to hose Provide backflow protection to hose connection. |  | Item
3.7.16 | Cold water filtration system Allow to service system. |  | Item
3.7.17 | Taps corroded. Allow to replace taps with new, stainless-steel taps |  | Item
3.7.19 | Bathroom mechanical extract not working Allow to supply and install new mechanical extract fan on the external facing wall to achieve a minimum extract rate of 15L/s to meet the guidance in Approved Document F. Make good the area around any penetrations internally and externally. |  | Item
3.7.20 | No mechanical ventilation installed to the galley kitchen Allow to supply and install new mechanical extract fan including penetration through wall fabric to achieve a minimum extract rate of 30L/s to meet the guidance in Approved Document F. Make good the area around any penetrations internally and externally. |  | Item
0
0
0

## Electrical
Council of the Isles of Scilly
Off Island Toilets and Fire Station
Schedule of Works
St Agnes Fire Station - Electrical
Duplicate item of work
Ref | Description | Quantity | Unit | Rate | £
3.7.5 | Incoming Data services cable sheathing degraded / cracking Allow to renew data services cable / provide protective sheathing. |  | Contractors Design
3.7.6 | PVC Distribution Board Allow to replace PVC distribution board with metal fireproof board in accordance with BS 7671. |  | Contractors Design
3.7.7 | Internal light fittings missing diffusers and no emergency lighting. Allow to supply and install diffusers to light fittings. Contractors design, supply and install new emergency lighting layout. |  | Contractors Design
3.7.8 | External lighting and photocell diffuser degraded Allow to remove external lighting and photocell diffuser and replace with new to match the existing. |  | Contractors Design
3.7.9 | Final circuit cables not supported Supply and install new conduits. Contractor to allow for re-routing cables within new conduits. |  | Contractors Design
3.7.10 | Inadequate socket outlets, additional required to prevent overload Provisionally allow to supply and install additional socket outlets, number to be confirmed by CA. |  | Contractors Design
3.7.11 | Intruder Alarm Fault Provisionally allow to repair / renew intruder alarm upon further investigations. |  | Provisional Sum |  | 1800
3.7.12 | Lightning Protection Provisionally allow to install lightening and surge protection in accordance with BS EN 52306 and BS 7671. |  | Contractors Design
3.7.13 | Electric hot water heater not working Supply and install new hot water heater. Contractor to allow for removal and disposal of existing. |  | Item |  |  | 0
3.7.18 | Electric heaters past economic life and poor condition Allow to strip and dispose of existing heat emitters. Supply and install new electric heat emitters to match existing configuration. Heater to be: Messrs, Dimplex, Millbrook House, Grange Drive, Hedge End, Southampton, Hampshire, S030 2DF, telephone, 0844 879 3589, being the Quantum Range. |  | Item
3.7.19 | Bathroom mechanical extract not working Allow to supply and install new mechanical extract fan on the external facing wall to achieve a minimum extract rate of 15L/s to meet the guidance in Approved Document F. Make good the area around any penetrations internally and externally. |  | Item
3.7.20 | No mechanical ventilation installed to the galley kitchen Allow to supply and install new mechanical extract fan including penetration through wall fabric to achieve a minimum extract rate of 30L/s to meet the guidance in Approved Document F. Make good the area around any penetrations internally and externally. |  | Item
0
0